BUTTE COUNTY

ENVIRONMENTAL HEALTH DIVISION

ANNUAL SMALL WATER SYSTEM INSPECTION REPORT

SYSTEM DEFICIENCY RECORD

Name of System    Gran Mutual Water System         System Number    04-00008

| Date Noted | Description of Defect or Hazard | Order No. | Confirmed Corrected |
| --- | --- | --- | --- |
| 11/4/03 | Booster pumps cycle very frequently. Determine reason why and repair as necessary | 3 | 9/1/05-variable pump installed at Pump #3 |
| 11/4/03 | Verify pressure gauge at booster station is working properly | 3 | 9/1/05 |
| 11/4/03 | Clean booster station area of debris | 3 | 9/1/05 |
| 11/4/03 | Repair leaky valve at booster station | 3 | 9/1/05 |
| 11/4/03 | Latch for new storage tank was unlocked at time of inspection. Insure against unwanted entry by securing latch. | 3 | 9/1/05 |
| 11/4/03 | Repair flap valve on storage tank discharge line to preclude entry by insects, etc. | 3 | 9/1/05 |
| 11/4/03 9/1/05 | Paperwork – Submit up-to-date emergency notification plan by January 1, 2004. Submit revised Sample Siting Plan by January 1, 2004 | 3 | 9/1/05-ERP was received from Randy Hill at time of inspection. Sample Siting Plan to be received by 10-31-05. |
| 11/4/03 9/1/05 | Storage Tanks – Storage tanks as well as their vents should be checked on a regular basis to insure they are free of holes/openings. Check and repair as necessary. Plug small holes on top of storage tank as observed at inspection. Prune or remove tree next to storage tank. Trees remain growing over top of tank. Growth over tank not only promotes entry of insects and vermin into the tank, but also makes storage tank more accessible to vandals. | 3 |  |
| 11/4/03 | Pressure Reducing Station - Unable to view at time of the inspection. The pressure reducing station must be accessible at the next inspection. | 3 | 9/1/05 Available at inspection |
| 9/1/05 | Observed leaks at storage tank furthest from pump station. Repair/replace. | 3 |  |
| 9/1/05 | Repair/replace gate valve at storage tank leaking | 3 |  |
| 11/4/03 9/1/05 | General - Pressure Vacuum Breakers (PVB) or Double Check Valves (DCV) have been installed on the water lines for the irrigation systems. A cross connection specialist must test PVB devices on an annual basis. Submit test results. This is a repeat violation and must be completed within the next 30 days. | 3 |  |
| 11/4/03 9/1/05 | Well – Construction equipment and debris should not be stored near well. Remove all equipment and secure well site by repair of fence. | 3 | 9/1/05-Some progress has been made in the clean up of the miscellaneous debris and equipment stored in the vicinity of the well. The storage sheds remain and removal of contents is reportedly taking place. Improvement is noted in appearance at well area. |
| 11/4/03 9/1/05 | Provide a copy of certificate for D-1 water distribution operator | -- |  |
| 9/1/05 | Install meters at homes and at well to monitor well production vs. individual homeowners’ usage. Track water loss and investigate cause; abate…repair leaks found. | 4 |  |
| 9/1/05 | Seal electrical box at well. Replace gasket and bolts/screws that have been stripped. | 3 |  |
| 9/1/05 | Replace silicone seal at well cap & casing | 3 |  |
| 9/1/05 | Provide emergency generator in case of power outage | 4 |  |

Order Number

1.	Serious health hazard; corrective action must be taken immediately.

2.	Critical system or operational defect &/or potential health hazard; must be corrected as soon as possible.

3.	System or operational defect &/or potential contamination hazards of lesser public health significance.  Must be corrected as workload permits.

4.	System or operational defect &/or potential health hazard - costly to correct - to be included in any long-range water improvement project.